## SCOPE
Annexure C - Landlord Scope of Works
SRG | [6 empty] | Date: 22/04/2026
Version: BCF- VER02.2 | [6 empty] | Revision: 2
Prepared By: Greg Dickson | [6 empty] | SRG Leasing Manager: Chris Alcock
Reviewed By: | [6 empty] | Landlord Contact: David Gorman
Signed by Tenant : | [6 empty] | Signed by Landlord:
|  | RESPONSIBILITY MATRIX | [7 empty] | HANDOVER CHECKLIST
|  | Completion of Works |  | Cost of Works |  | REQUIREMENT |  | ADDITIONAL TENANT COMMENTS | LANDLORD RESPONSE | Works Complete |  | Comments
|  | LL | T | LL | T
1 | Consultants | [8 empty] | YES | NO
1.01 | Base Building Architect | X |  | X |  | Base building requirements incorporating Tenant layout/ requirements. Landlord to supply plans to Tenant in PDF and DWG format. Base Build Plans to include at minimum: Site plan, floor plans, elevations, Reflected Ceiling Plan (RCP) to show internal roof / ceiling heights Electrical & Data, Fire Services Mechanical Services Hydraulic Services pylon sign design and location, bin storage and any other licenced areas, traffic management site plan showing swept paths for delivery trucks. Other plans may be requested to ensure Tenant can complete appropriate layout plans.
1.02 | Fit-out Architect | X | X | X | X | Supply plans in PDF and DWG format. (Plans to include at minimum- site plan, floor plan incl fixtures, elevations, electrical, data including pylon sign design and location, bin storage and any other licenced areas, tenancy plan to show services locations including FHR's, DB location, amenities details, RCP plan to show internal roof heights, traffic management site plan showing swept paths for delivery trucks.) |  | Subject to SoW, Tenant to provide plans for retail layout and elevations for signage mock up for inclusion in LL plans and approvals.
1.03 | Electrical Engineer | X |  | X |  | Base building & Tenant ’s layout/requirements Provide all Plans and equipment specifications.
1.04 | Structural Engineer | X |  | X |  | Base building requirements
1.05 | Traffic Engineer | X |  | X |  | Base building & Tenant ’s layout/requirements (delivery truck size minimum 12.5m MRV), refer Delivery requirements sheet v1 of 22/10/2025 |  | N/A - Existing trading site, expansion utilsiing same delivery access roads.
1.06 | Mechanical Engineer | X |  | X |  | Base building & Tenant ’s layout/requirements. Provide all Mechanical Services Plans and equipment specifications.
1.07 | Hydraulic Consultant | X |  | X |  | Plans to suit all hydraulics
1.08 | Seismic Engineer (if applicable) | X |  | X |  | Base building requirements
1.09 | Accessibility Consultant (if applicable) | X |  | X |  | Base building & Tenant layout requirements
1.1 | Fire Engineer | X |  | X |  | Base building to Tenant ’s layout (if applicable). Provide copies of FER where applicable and Fire systems plans.
2 | Permits / Fees
2.01 | Development Application - Permitted Use | X |  | X |  | Provide approved copy for Tenant records.
2.02 | Development Application - Building | X |  | X |  | For Tenant approval prior to submission.'Provide approved copy for Tenant records. For existing buidling provide copy of existing DA - Where any changes to existing DA are required then Landlord to seek approvals.
2.03 | Development Application - Signage | X |  | X |  | For Tenant approval prior to submission. Includes any Authority approvals and or Body Corporate. Provide approved copies for Tenant records. |  | LL to also confirm centre signage opportunities in addition to tenancy signage. Tenant to provide tenancy mock up for approval. Approvals by LL, signage supply and install by Tenant.
2.04 | Building Approval (To include Tennant ’s Fit out design) | X |  | X |  | Arrange all building permits and consents required to complete the works including the final Occupancy Certificate for the Tenancy that includes the Retail fixture layout ready for trade.Provide approved copies for Tenant records.
2.05 | Asbestos Report | X |  | X |  | If pre 2004 construction, Asbestos report is required |  | LL to confirm date of construction and Asbestos free.
2.06 | NCC Part J (Energy efficiency) Compliance Report | X |  | X |  | Provide DtS Compliance report or JV3.
2.07 | Building Operations and Maintenance Manual | X |  | X |  | Copies of all Plans, Approvals, Equipment Specifications, manuals, deliverables and Reports as per attached SRG Building O&M Manual requirements.
2.08 | Builders Insurance | X |  | X |  | Provide copies of builders works insurance prior to commencement of LL works
3 | Demolition Works
3.01 | Demolition works | X |  | X |  | Any demo works required to allow construction / fit out to Tennant ’s plans and specifications (incl. but not limited to: internal walls, doors, redundant services, fixtures / fittings, signage) Removal of existing gas systems and appliances. |  | Demolish IT wall as per tenant layout. Relocate any services running throughout or attached to IT Wall. Remove existing data cabling in new tenancy back to its supply point. Remove all obsolete services and cabling from roof space and tenancy walls. Tenant will demolish current BCF tenancy toilet and team room and make good floor / wall and cap any services.
4 | Base Building Works
4.01 | The building's primary structure | X |  | X |  | Structural works Civil Works & Foundation works Insulation to External Walls & Roof to meet NCC minimum total R-Value for applicable climate zone, insulation to comply with AS/NZS 4859.1 Internal Perimeter Wall linings to be constructed to the underside of Roof
4.02 | Road access to site and building | X |  | X |  | sealed road access including to the loading bay/rear Dock, and loading bay hardstand. |  | Existing road access - No change
4.03 | Structural Walls | X |  | X |  | Building's primary structure |  | Existing Base build structure.
4.04 | Tenancy Floor structure | X |  | X |  | Uninsulated slab on grade, other than where specifically required by NCC J4D7 'Concrete slab minimum requirements 5kN/M2 |  | Existing Slab - LL to confirm strength.
4.05 | Electrical & Data Conduit Works - Pre Concrete Slab TBC by Tenant | X |  | X |  | Install Conduits into Slab to Island Joinery 1. Sales Counter 2. Fishing Reel Counter/Workshop |  | N/A - No slab conduits, all data and electrical from ceiling.
4.06 | Recessed Entry Matt Internal - New Slab Only | X |  | X |  | Recessed Entry Mat - low profile aluminium matting system recessed into a Mat Well, Made from a combination of clear anodised aluminium, and a marine grade carpet. Rubber Backed. |  | N/A - Current BCF entry to be utilised - Any new Matt by Tenant as part of exist BCF tenancy improvements.
4.07 | Roof & Façade | X |  | X |  | Roof to NCC2022 J4D4 • Galvanised roof sheeting is not permitted without infrared reflective roof coating in climate zones 1 though 6 to achieve compliance to NCC2022 J4D4. • No skylights are permitted • Roof insulation must extend over BoH zone, even if not otherwise part of conditioned space. |  | Existing Roof to be utilised - Any leaks to be rectified by LL. Improvements to comply with NCC2022 J4D4 by LL if required by local authoriteis as part of building approval.
4.08 | Roof Access, walkway's, anchor Points & fall Protection | X |  | X |  | ''Suitable safe access in accordance with Australian Standards to air conditioning/Solar equipment plant for future service and maintenance requirements - including but not limited to: Roof access Ladder access with security Measures Walkways Anchor points Edge protection To suit any equipment & Plant requirements in accordance with applicable AS/NZS standards. Provide installation / test certificates.
4.09 | Delivery Dock Awning | X |  | X |  | Clearance height min 5000mm (awning dimensions per approved plans) External dock areas will be fitted with LED security flood lights on motion sensor with a minimum of 50W (6,000 lumens) on timers during out of hours trade hours (7pm - 5am daily) unit spec to be provided to tenant for approval prior to installation and confirmed timer hours confirmed prior to final programming. Colour Temperature: 4000K IP65 or higher for weather resistance |  | Existing Awning to be utilised. Lighting improvements by LL. Repair and secure any damaged insulation
4.1 | Entry Awning | X |  | X |  | The retail shopfront areas will be fitted with LED security flood lights on motion sensor with a minimum of 50W (6,000 lumens) on timers during out of hours trade hours (7pm - 5am daily) unit spec to be provided to Tenant for approval prior to installation and confirmed timer hours confirmed prior to final programming. Colour Temperature: 4000K IP65 or higher for weather resistance |  | Existing Entry awning and lights to be utilised, exist awning lights are in common area, owned and maintained by LL. Not connected to Tenant EDB. LL to confirm where entry awning lights are fed from. Repair and secure any damaged insulation
4.11 | Roller Door - Delivery | X |  | X |  | Heavy Duty industrial motorised Roller Door - Colour TBC with Tenant (Light Grey) Painted light colour for reduced Solar Absorbance <0.45. Colour to be approved by Tenant. All roller doors to have flexible foil-faced insulation installed with min. 10 year warranty. All roller doors must have brush seals to sides / top and rubber/poly seals to bottom. Manual Override Chain Minimum 3m wide x 3.2m high Reinforced base and track and fitted with 2 Xtratec brand floor anchor locks and kink bolts at base of door. (XTRA1A) Keyed isolator switch to the roller door motor controls - With hinged Warning Sign over Controls master key padlock for each floor anchor with common key. Wind Locks on Roller Door Additional Floor anchors if door width > 4 metres 1.4metres apart |  | Existing Roller and Motor to be utilised. Additional Floor Anchor Locks x 2 to be installed@ approx 1m spacings Keyed isolator switch and cover required
4.12 | Delivery Dock - Access Ground Level | X |  | X |  | Ground level to permit manual pallet delivery of pallets up to and including 1500kg in weight into tenancy. No lip & smooth egress Entry Dock Access to Tenant dock must be covered and well illuminated to AS/NZS, if truck is not able to load directly to Tenant dock. (Ie path way or loading corridor) |  | N/A - Existing Elevated dock
4.13 | Delivery Dock - Access Elevated | X |  | X |  | Elevated Loading Dock: Design ramp with a gradient compliant with building codes (maximum 1:14 for accessibility). Pallet Delivery Access: Ensure ramp width accommodates pallet jacks and forklifts. Weight Capacity: Construct dock and ramp to support delivery of pallets up to and including 1500kg in weight into tenancy. Safety Features: Install gates, handrails, and edge barriers meeting safety standards (AS/NZS 1657). Seamless Transition: Ensure no lip or obstruction at entry/exit points; maintain smooth egress. Durable Surface: Use non-slip, weather-resistant materials for ramp and dock surfaces. Permits & Compliance: Obtain necessary permits and ensure compliance with local regulations. |  | Existing Elevated Loading Dock to be utilised. No Ramp, existing stair access. LL to confirm weight capacity
4.14 | Loading Bay Access | X |  | X |  | Minimum clearance of 2500 mm in width from the loading bay to the retail dock area Designed to accommodate pallet access including oversized pallets using a pallet jack. Access to Tenant dock must be covered and well illuminated to AS if truck is not able to load directly to Tenant dock. (Ie path way or loading corridor) Where Tenant dock and tenanacy are not adjoining, suitable path of travel with clear access to accomodate oversize pallets using a pallet jack is required. |  | N/A - Loading dock has direct access to BOH receiving.
4.15 | Access ways (Lobbies, stairs, corridors) | X |  | X |  | To suit Tenant’s Layout & Landlord to provide disabled access throughout iaw DDA.
4.16 | Under Slab Plumbing & drainage including Storm Water | X |  | X |  | To suit Tenant’s Layout |  | Existing in slab plumbing and draining service points to be utilised. LL to cap any unused services.
4.17 | Above slab Hydraulics including Storm Water | X |  | X |  | To suit Tenant’s Layout |  | LL to cap any unused services.
4.18 | Double Entry Doors (Automatic) | X |  | X |  | New Dorma automatic doors (as per plan) (Dorma or equivalent) with vision rail at 1.0m fitted with EL-301 door operator. Minimum 1900mm Wide Door opening, 2700mm Door Height with fixed glazing side panels and minimum 600mm highlight above. Must have Framed Sliding Doors. New Dorma automatic doors with electric EL-301 door operator to the tenancy entry as indicated the Base Plan Doors and activation mechanisms to comply with relevant Australian Standards including AS5007, AS1428.1 and the NCC. Doors to be fitted with: (A) 1 x LW3541RL1SC Escape Lever Lock, if emergency door adjacent to auto doors. If no emergency door adjacent to auto doors then a push button emergency switch is to be installed. (B) 1 x LWSP3540- LSSC Strike Unit, (C) LIAL515004 Outside spring key switch (Lock It Well), (D) LIAL545021 Inside four position switch (Lock It Well), Button installed to solid wall (E) External security cover plate fitted over locking mechanism to prevent break in, (F) Weather strips to prevent vermin and water entering the building, (G) Install 75mm (Min) solid Frosted, non-transparent vision strip (H) 3M Security Film installed to the inside of the glazing, (I) Ram Guard Kit (300mm 50mm x 50mm black square tubing with caps installed to Slab) (J) Power connected and commissioning completed (k) Crim safe on Front Doors & Glazing - TBC by tenant |  | Current BCF Tenancy entry to be utilised with existing doors. LL to remove redundant auto doors and enclose opening with glazing to match existing shopfront.
4.19 | External Exit Doors | X |  | X |  | Metal Sheathed Solid Core Concealed Hinges Full Door Length Striker Plates 3 x Hinge Pin Panic Bar Locking System - Rivers Model F 4 point locking system (KL system ONLY for desiganted TM entry door, no external entry otherwise) Peep Hole when designated TM entry/exit point Fire Exit Signage Weather Seals |  | Replace all existing external exit doors to both tenancies | Replace doors to new tenancy space only
4.2 | Shop Front Glazing | X |  | X |  | Entry Minimum 5400mm Wide x 3400mm High All glazing to be clear, without tinting or colouring Entry doors and fixed glazing installed throughout the tenancy to be clearly marked with a 75mm (Min) solid Frosted, non-transparent, contrasting line across their full width. In accordance with the Building Code of Australia AS1428.1 Shopfront Swing Doors (if required) to be fitted with (A) Full Door Length Striker Plates (B) No Door Handle Externally (C) Weather Strip As per DtS Glazing & Façade assessment and/or JV3. Note: • Generally avoid west-facing glazing where possible. • Where glazing not required as part of fitout, blank off glazing with insulated stud wall to external wall requirements. Consider ventilation of cavity and condensation risk in relevant climates. |  | Existing Shopfront glazing. - Tenant will Vinyl external.
4.21 | Shop Front Glazing - Glass Specification | X |  | X |  | Viridian Glass – Supply and install “Viridian Assault guard Ulta 10” clear glazing and required frames/mullions to the entry of the tenancy. To include all glazing at entry, auto doors, side panels, highlights and any exposed glazing throughout the tenancy. |  | N/A - Existing shopfront glazing to be utilised.
4.22 | 3M Security film - if Viridian Assault Guard is not installed | X |  | X |  | 3M Ultra S800 security film with 3M IPA (Clear) security film internally to all glazing at entry, auto doors, side panels, highlights and any exposed glazing throughout the tenancy. 3M Safety S70X (external) on the outer surface. Installation to ensure film is covering to edge of glass, removing glazing rubbers if necessary. To include all glazing at entry, auto doors, side panels, highlights and any exposed glazing throughout the tenancy. |  | N/A - Tenant to apply vinyl to external of glazing
4.23 | Security Mesh | X |  | X |  | Black security mesh (to Australian standard AS5039-2008 and AS5041-2003) To include all glazing at entry, auto doors, side panels, highlights and any exposed glazing throughout the tenancy. |  | N/A - By tenant to current BCF tenancy if required.
4.24 | External Security Shutter - If required, TBC by Tenant | X |  | X |  | External motorised heavy duty extruded aluminium Black security shutter. Shutter to cover entry glazing, auto door, highlights, and sidelights. Motor to be wired to a power point adjacent to opening or power feed to switch location. Shutter to be operated via secure key switch mounted externally (Lock it well type). A secret manual override to operate shutter in event of power outage to be included, |  | N/A - Existing BCF Teanncy entry to be utilised
4.25 | Inner tenancy & access security | X |  | X |  | Any potential access within the roof space between adjoining tenancies to be prevented by materials approved by Tenant |  | Exist adjoining IT walls are full height.
4.26 | Fixed bollards | X |  | X |  | Protect all external glazing and exit doors spaced at maximum 1.4m centres Bollards to be installed to Edge/corner of Roller Door openings Bollards to be 150mm diameter pipe core filled with concrete and rounded top finish Installed 1200mm above and 700mm below ground level and to include a concrete footing at a minimum depth of 500mm All non-removable bollards to be Powder Coated BCF Orange PMS151C |  | Additional bollards required to shopfront to meet requirement. All bollards to front of both tenancies to be painted / powder coated BCF Orange.
4.27 | Removable bollards | X |  | X |  | 90mm removable bollards with padlocks spaced at maximum 1400mm centres to protect the roller door. Recessed with Cover plates to be used over holes when bollards are removed Bollards to be no more than 17kg in weight. Storage bracket to be installed in the dock area with wall protection to store bollards when not in use. Bollards to be powder coated Dulux Safety Yellow – (Pantone PMS 7405). |  | N/A - Elevated dock, no vehicle access to roller.
4.28 | Open Ceiling | X |  | X |  | Open ceiling to minimum 6000mm FFL to underside of Services |  | LL to confirm minimum height to underside of existing services for acceptance by Tenant.
4.29 | Emergency Lighting | X |  | X |  | LED Emergency Exit and evacuation lighting in accordance with AS2293.1. Location of emergency exit and evacuation lighting to take into consideration fixture layout and permitted use. Exit Lights - Clevertronics Ultrablade Pro Surface Mount Provide test switch facilities on distribution boards to comply with AS2293. Wired back to the Tenancy EDB Provide a completed log book (General Lighting Service or equal). New stores to be provided with the following Non-Maintained Emergency Lighting: Tiled or Plaster Ceilings - Clevertronics Lifelight Recessed High / Exposed Ceilings - Clevertronics Lifelight Surface Mount Warehouse Lens Light Existing emergency lighting can be retained provided: • All existing emergency lighting is LED • All existing emergency lighting is not configured as “Maintained” |  | Existing Exit and emergency LED lighting may be reused, reconfigured by LL as required for compliance to Tenant layout. Where additional EEL required this is by LL to suit tenant layout.
4.3 | Fire Services | X |  | X |  | All wet and dry Fire Services equipment required to obtain compliance for the tenancy including but not limited to hydrants, fire panels, hose reels, sprinklers, extinguishers, alarms, smoke detectors, etc as required to achieve compliance. Design to ensure captures building & Tenant ’s fit out, fixture layout/requirements and any solar generation or battery storage systems. |  | No Wet fire. Existing detection to be reconfigured as required for compliance. Relocate / modify services as required to suit tenant layout. Central FIP to centre.
4.31 | Fire Services | X |  | X |  | Where Fire Hydrants are to be enclosed in a Cupboard, cupboard to match adjacent wall colour - To be approved by Tenant |  | N/A - Hoses are open, no cupboards required.
4.32 | Hoarding / Fencing | X |  | X |  | Supply and installation of full-height hoarding around the premises, to meet building regulations, or as part of construction or renovation works. Hoarding to be professionally installed to meet safety standards, local council requirements, and any other applicable regulations. Supply and install temporary fencing around the external boundaries of the leased premises, if required for security, safety, or compliance with local regulations. Temporary fencing to be erected in accordance with local authority requirements and safety standards.
4.33 | Air Tightness | X |  | X |  | General construction methodology to consider best practice air tightness including roof / wall detailing, door seals etc. Blower door testing results is to be provided to Tenant for acceptance prior to handover. Tests to be completed by qualified professional (ATTMA registered tester or equivalent) in accordance with ATTMA standards General Target of 5 m3/hr/m2 or 2.5 ACH* at 50 Pa. Maximum acceptable rate of 10 m3/hr/m2 or 5 ACH* at 50 Pa. Notes: • * ACH rate based on 50m x 30m x 5m ceiling, 1,500 sqm typical footprint |  | N/A - Existing tenancy.
5 | External and Site works
5.01 | External Walls | X |  | X |  | 150mm precast concrete with stud frame, insulation and plaster, minimum total R-1.4 Alternatively insulated sandwich panel is also acceptable. Framing to engineers specification. |  | Existing precast external walls. Make good any damage from previous tenant.
5.02 | Foundation works | X |  | X |  |  |  | Existing - as is
5.03 | Sealed Road Access | X |  | X |  | Prior to Landlord Handover |  | Existing - as is
5.04 | Delivery Doc Access | X |  | X |  | Road access suitable for MRV Delivery Vehicle, including driveway crossovers. Overall length of vehicle including cabin & PTG lowered – 14.1m up to average weight of 16.0 tonnes to 24.0 tonnes Ensure applicable surface to suit trucks, forklift and walkie stacker use Minimum clearance Width to accommodate Truck 2.5m wide Minimum clearance Length of loading bay 15.5m |  | Existing raised dock. Repair and repaint handrails as required. Concrete repairs as required to ensure safe and smooth receiving surface for pallet jacks.
5.05 | Line Marking | X |  | X |  | Line Marking to meet Australian standards and to include nonslip aggregate. Prior to Practical Completion.
5.06 | Hard stand (carpark) | X |  | X |  | Bump stops installed and appropriate safety markings applied for safety and trip hazards (painted yellow or safety bump stops) prior to Practical Completion. |  | 2204GD - Tenant to paint the C&C bays, all other carpark works remain LL.
5.07 | Loading bay hardstand | X |  | X |  | Bump stops installed and appropriate safety markings applied for safety and trip hazards (painted yellow or safety bump stops) prior to Practical Completion.
5.08 | Bin Enclosure | X |  | X |  | A Colourbond lockable bin enclosure located at the loading dock of the tenancy to house the General and Recycling bins as indicated on the Licenced Areas Plan Dimensions of the Bin Enclosure are site specific and will need to be discussed with Tenant for approval prior to installation. Minimum sizing - 5400mm L x 2200W x 2000H Double swing Door allowing for 2 x 4.5m³ Bins - Colour Bond Monument Grey |  | N/A - No enclosure required, licenced area for bin storage behind tenancy per tenant site layout.
5.09 | Mail Box as required by local Postal authority | X |  | X |  | The Landlord is to provide the necessary mail facilities as required by Australia Post |  | Per existing arrangements.
5.1 | Any Steps / Raised Pathways/ Access To Tenancy | X |  | X |  | Prep & Paint any potential trip hazard / Steps, within Tenancy and external travels of path to Tenancy to be painted Safety Yellow Raised Pathways to ensure compliant Hand railing is installed |  | Make good pavers to front of both tenancies. 2204GD - To be completed by LL as part of paver replacement to entire centre, Timing to be agreed.
5.11 | Landscaping | X |  | X |  | To be low height (max 300mm) so as to not obstruct sight lines to buildings Landscaping to grow to a maximum of 30cm, maintenance contract for landscaping to be in place
5.12 | Pylon Signage - Communal Pylon | X |  | X |  | Faces supplied and installed. Pylon signage to be reviewed & approved by Tenant. Pylon to be illuminated. Refer BCF Signage Guides for specifications
5.13 | Pylon Signage - Stand Alone Dedicated | X |  | X |  | Pylon Structure by Landlord including footings, cladding, Engineering Faces supplied and installed Pylon signage design to be reviewed & approved by Tenant. Pylon to be illuminated. Refer BCF Signage Guides for specifications |  | N/A - No Stand alone pylon.
5.14 | Pylon structure and signage zone structure assessments (If existing) | X |  | X |  | Existing pylon structures or signage zone structures to be assessed for sound structural integrity by a qualified engineer, report to be provided to Tenant before lease commencement.
5.15 | Disabled Parking Bay | X |  | X |  | Provide Disabled Parking bay(s) in accordance with local regulations in an appropriate location to access Tenancy |  | Utilise existing adjacent to ramp.
5.16 | Gas Decanting Designated Licensed Area | X |  | X |  | Landlord to provide DA approved Designated area to meet specific exclusion zone requirements such as fire hydrants, electrical sources, open drains and door openings. See Tenant for further requirements. 'Area requires Origin Energy Approval, to meet AS normal area is either 2 car spaces in front of Tenancy or specific designed area adjacent to Tenancy approx. 4mx4m refer to licensed area plan Gas Decanting Area required to be sealed Road or concrete slab - refer Gas Decanting Area requirements sheet |  | To front of tenancy away from entry doors. 2204GD - Location to be agreed between parties. | Sill pending decision by HN property manager
5.17 | Gas Decanting Works (See TAB below GAS DECANTING) | X |  | X |  | Complete the car park line marking, compliant traffic barriers (Armco railing or similar), Powder Coated BCF Orange PMS151C Dulux Bollards Concrete filled install to the area - Bollards Maximum 1200mm spacing and meet AS Origin Gas Standards. If bollards are surfaced mounted - concrete filled, chem set fixing with 25mm plate As per Origin Standards Clear Access from tenancy to gas decanting area including any requirements such as ramps, pedestrian crossings |  |  | As above
5.18 |  |  | X |  | X | Installation of Gas Decanting appropriate signage |  |  | As above
5.19 |  | X |  | X |  | Supply and install an overhead shade structure as indicated on the Licenced Areas, incl engineering certification. Structure to Tenant Design & Requirements |  |  | As above
5.2 | Gas Decanting Structure - Civil works | X |  | X |  | Engineering & Installation of Footings required for Structure Installation |  |  | As above
Services
6 | HVAC
6.01 | Air Conditioning (General) | X |  | X |  | To suit Tenant ’s requirements & Layout (refer plans and supporting documentation) including BOH Doc Area Unit to be completely separate from other tenancies Height no lower than 6000mm above FFL HVAC Temperature, and CO2 Sensors to be located at approx. 1800 FFL on internal columns and walls only (not external walls), and located away from sources of heat, dust, Audio Visual, signage etc. Balance & Commissioned Minimum of one (1) year manufacturer’s warranty Final ducting plan to be provided to Tenant for approval Ventilation systems to be designed to NCC and AS 1668. Mechanical HVAC system to comply with energy efficiency requirements of NCC Section J 2022 Part J6. Ventilation must have bushfire mode to enable the temporary closure of all outside air intakes. Any existing Gas heating systems are to be replaced with electric. |  | Based on age of existing units, replace all rooftop packaged units to both tenancies. 2204GD - Replacement by LL to align with building HVAC replacement. Timing to be agreed. LL to provide condition report for tenant review. Modify existing ductwork as required to suit tenant layout. Clean existing ductwork
6.02 | HVAC Design Conditions | X |  | X |  | Internal Conditions 22°C ± 1.5°C Dry Bulb. Generally 50% RH target (Humidity not controlled). Wider deadband (nom. 18-26°C) for energy efficiency used at Tenant’s discretion Ambient Conditions: As per AIRAH DA9 Critical Process Noise Criteria Sales Floors: NC 40 Storage Areas: NC 50 Zoning Tenancies must have Air conditioning temperature control specific to that zone only (i.e not shared with other tenancies) and for each discrete room. Load Calculations CAMEL or Carrier HAP load calculations must be provided to Tenant for approval including all assumptions, and retained with O&M Manuals. Noise Criteria: NC35 throughout. Loading Dock area NC40.
6.03 | Air Conditioning system and controls. | X |  | X |  | Rooftop package units, Temper zone econex series or similar. R32 inverter or equivalent. Fusion Modulair also accepted. Air conditioning system with high efficiency design including Inverter compressor or digital compressor, Electronically Commutated (EC) plug or multi speed evaporator fan and EC Plug or variable speed supply air fan, Electronic Expansion Valves, final specifications to be approved by Tenant. Supply and install adjustable dampers connected to a CO2 monitor on the outside air intake for the A/C units servicing the tenancy. CO2 Fresh air control with min 2 x CO2 sensors (averaging). Integrated with PAC with pressure-based spill air including variable speed fan if required Supply and install air conditioning controller in manager’s office and to include a 7-day 24 hour time clock. The HVAC system shall have an economy cycle option and be fitted for connection to Tenant building management system. Economy cycle shall be included where required by NCC 2022 Part J6D3 & Table J6D3. For ducted package units, supply and install fresh air dampers with adjustable position from 0% to 100% to allow for full fresh air economy cycle control. The economy cycle operation shall be able to be control by a BMS where the controllers are to be programmed with standard applications that can be selected in the user interface, via BACnet communication
6.04 | Ductwork and Air Diffusion | X |  | X |  | Any above-roof ductwork to coated with infra red reflective of solar absorbance <0.45 as per roof sheeting. 'To Retail Space: - Galvanised steel rectangular, insulation in accordance with NCC J6D6 and/or internally insulated where required for acoustic performance. - Fabric duct by specific approval only. - Proprietary Fusion HVAC also accepted. Underside diffusers not to be used, side grills / diffusion required. To BOH / Team Room / Offices / Amenities - Galvanised steel rectangular from roof, internally insulated where required for acoustic performance. - R-1.0 flex duct where required. Max length 4m with no joins permitted. Flex duct only permitted above ceilings (not exposed) between duct and air diffusion. Flex duct must be fully extended with all necessary supports to mitigate vibration, movement, airflow constriction and/or leakage. Refer AIRAH Guide - Egg crate grilles for exhaust / return air. - Makeup / spill air transfers generally via Door grilles. Egg crate with cushion head box and flex for secure spaces (or otherwise as required). All air diffusion equipment is to be a high-quality reputable name brands such as Holyoake, Fantech, Price Industries, Trox, Smartair or equivalent. Air ventilation products are to be a high-quality reputable name brands such as Fantech, Systemair, Fanquip, Blauberg or equivalent. |  | Existing Ductwork and diffusion to be utilsied within tenancies. Alterations to suit new tenancy layout by LL and as required for compliance. Remove redundant ducting where existing rooms are demolished. Clean tops of ductwork in new tenancy to remove dust and debris.
6.05 | Mechanical - Air Curtain over Store Entry | X |  | X |  | To suit Tenant’s Layout (Min High Star Energy Rating system) Low Noise Power supply to unit from EDB , Remote controller Specification to be Approved by Tenant Climate zones 1,2,3 and 7 only. |  | N/A - Existing entry to be utilised.
6.06 | Air Conditioning Split Systems - Team Room | X |  | X |  | To suit Tenant’s Layout (Min High Star Energy Rating & Min 6KW reverse cycle split system) Fixed rate fresh air integrated with AC run time.
6.07 | Air Conditioning Split Systems - Managers Office | X |  | X |  | To suit Tenant’s Layout (Min High Star Energy Rating & Min 2.5 KW reverse cycle split system) Fixed rate fresh air integrated with AC run time.
6.08 | Air Conditioning Split Systems - Area Managers Office (If applicable) | X |  | X |  | To suit Tenant’s Layout (Min High Star Energy Rating & Min 2.5 KW reverse cycle split system) |  | N/A - No Area Managers office
6.09 | Air Conditioning Split Systems - Click & Collect (If Enclosed Ceiling) | X |  | X |  | To suit Tenant’s Layout (Min High Star Energy Rating & Min 2.5 KW reverse cycle split system) If enclosed Ceiling |  | N/A - Click and collect to have open ceiling
6.1 | Mechanical Exhaust - Bathrooms | X |  | X |  | Mechanical ventilation in accordance with the Building Code of Australia Fan Grill Fixed rate exhaust with a timed (adjustable) movement sensor or push button switch installed Makeup air to be drawn from conditioned spaces via appropriately sized door grilles, undercuts and/or above-ceiling transfers etc.
6.11 | Unit Commissioning & Setup | X |  | X |  | Include Balance and Commissioning, Timer Setup, Warranties, Equipment List, Manuals, Recommended Servicing Commissioning in accordance with AIRAH DA27. Reports to be provided to tenant prior to handover.
6.12 | Existing Airconditioning - Remove if not Existing system or equipment | X |  | X |  | To suit Tenant's requirements & Layout (refer plans and supporting documentation) Provide a detailed list of all air conditioning equipment servicing the tenancy Provide Report on existing unit confirming to confirm life span Mechanical specifications of existing to be provided to Tenant for approval Unit to be completely separate from other tenancies height no lower than 6000mm above FFL Wall sensors to be higher the Fixtures Balance & Commission. Generally to AIRAH DA27. Refer detailed checklists to be returned to Tenant prior to handover. All existing equipment must have comprehensive commissioning conducted prior to handover as if it were a new installation. Minimum of one (1) year manufacturer’s warranty For any existing equipment retained as part of the new lease, prior to SRG taking occupancy all equipment is to have a comprehensive annual service (refer AIRAH DA19) conducted generally including ductwork and coil cleaning, filter replacement, any relevant lubrication and tensioning and calibration / verification or replacement of all BMS / thermostat control sensors. |  | Replace Rooftop package units, Existing Ductwork and diffusion to be utilsied within tenancies. 2204GD - Replacement by LL to align with building HVAC replacement. Timing to be agreed. LL to provide condition report for tenant records. Alterations to suit new tenancy layout by LL and as required for compliance. Remove redundant ducting where existing rooms are demolished. Clean tops of ductwork in new tenancy to remove dust and debris.
6.13 | Building Management System (BMS) |  | X |  | X | Installation of Building Management System per SRG BMS Specification |  | N/A - Not required
6.14 | Approved Refrigerants | X |  | X |  | Generally R-32, R-454, R-290 (Propane) or R-744 (CO2) must be used in all HVAC, DHW and appliances (including fridge/freezers). Other refrigerants may be used by specific Tenant approval only.
7 | Electrical |  |  |  |  | To Tennant ’s Spec & Layout (refer plans and supporting documentation)
7.01 | Electrical Supply | X |  | X |  | The Landlord to supply and install 100 free amps per phase (e.g. excluding mechanical equipment), three phase power supply for Tenant requirements (refer plans and supporting documentation for tenant requirements) 'The Landlord shall provide a separately metered tenancy with CT meters. NMI and meter numbers to be provided to Tenant at least 8 weeks out from PC so electricity account can be set up for transfer from Landlord. |  | Existing electrical supply to tenancy to remain, both tenancies to maintain separate supplies. LL to provide NMI details to new tenancy for roll in by tenant.
7.02 | Electrical Distribution board | X |  | X |  | Supply and install 1 x Switchboard, to AS/NZS 61439, with internal busbars, minimum 48 pole Excluding Mechanical, 72 pole pending Mechanical requirements, equipped with Surge and Residual Current Device protection; switchboard to be located as indicated on the Electrical Plan. (refer plans and supporting documentation) Provide test switch facilities on distribution boards to comply with AS2293 Power metering: Comprehensive Metering (Modbus or BACNET) AS 62053-22 (Class 0.5) capable of measuring voltage, current, power factor, active and reactive power, total harmonic distortion, and energy consumption. • Tenancy Supply • MSSB • Solar PV Generation • (virtual meter) Tenancy Total usage (before PV offset) Basic Metering AS/IEC 62053-21 (Class 1) compliant kWh only. • General Power • General Lighting • DHW • Dumb Waiters • Escalators • Elevators (inc. Goods Lifts, Dock Lifts) • EV Charging • BoH Electric Walkie Stacker Charging |  | Existing 42 pole EDB and metering to be utilised. LL to ensure compliance to AS/NZS 61439 Provide test switch facilities on distribution boards to comply with AS2293. Remove / relocate breaker panel from IT wall to existing EDB location.
|  | X |  | X |  | Electrical Distribution board to be Key Lockable, 2 x sets keys to be provided.
7.03 | Thermographic testing of Electrical Boards |  | X |  | X | Thermographic testing to be completed following tenant fit out, prior to opening. |  | By Tenant
7.04 | Electrical Cabling - Open Ceiling | X |  | X |  | Electrical cabling on cable trays to be installed and terminated safe along roof line for later connection by others. Cabling must be neatly stored out of sight along the purlins/beams. Locations as indicated on the Electrical Plan.
7.05 | Electrical Cabling - Suspended Ceiling | X |  | X |  | Electrical cabling on cable trays to be installed and terminated safe above the ceiling grid for later connection by others. Locations as indicated on the Electrical Plan.
7.06 | Cable Tray Covers | X |  | X |  | All vertical/horizontal wall trays to include covers to full height All cable trays lower than 4000mm AFFL throughout the tenancy to include covers.
7.07 | Front Counter - Circuits | X |  | X |  | Separate dedicated circuits for the sales counter and parts counter as indicated on the Electrical Plan. Cabling to be left with a 10m tail for later connection at the setup. |  | N/A - Existing front counter location to be utilised
7.08 |  | X |  | X |  | 4 x Dedicated and 1 x General - Sales Counter |  | N/A - Existing front counter location to be utilised
7.09 |  | X |  | X |  | 2 x Dedicated and 1 x General - Click & Collect Counter |  | N/A - Existing front counter location to be utilised
7.1 |  | X |  | X |  | 1 x Dedicated - Front Counter Fridge |  | N/A - Existing front counter location to be utilised
7.11 |  | X |  | X |  | 1 x General - Multi function printer |  | N/A - Existing front counter location to be utilised
7.12 | Conduit Works - Pre Concrete Slab | X |  | X |  | Install Conduits into Slab to Island Joinery 1. Sales Counter 2. Fishing Reel Counter/Workshop |  | N/A - Existing front counter location to be utilised
7.13 | Retail - Dropper Circuits | X |  | X |  | General power circuits for droppers throughout the Retail & Dock Areas as indicated on the Electrical Plan. Dropper cabling to be left with a 10m tail for later connection at the setup. As per electrical plan. |  | LL to Allow for qty of droppers as indicated - exact locations TBC by tenant following retail plan development.
| sunglasses stand | X |  | X |  | 1 x Circuits Per Stand linked to lighting Circuit
| Fishing Bay Fixtures | X |  | X |  | 1 x Circuits Per Row linked to lighting Circuit
| Change Room | X |  | X |  | 1 x Circuits Per Room linked to lighting Circuit
| Fishing Real Counters | X |  | X |  | 2 x Dedicated Power Circuit to 5 x DGPOs
| Bait Freezer | X |  | X |  | 1 x Dedicated Power Circuit to EACH freezer
| Navigation Unit | X |  | X |  | 1 x Power Circuit to DGPOs
| Webber Pergola | X |  | X |  | 1 x Circuits linked to lighting Circuit
| Rope Wall | X |  | X |  | 1 x Power Circuit to DGPO - 1300 high to above Draw
| Home & Fridges Version A | X |  | X |  | 1 x Power Circuit per bench ( average 2 to 6 benches)
| 4x4 Display | X |  | X |  | 1 x Power Circuit to DGPO
| Ute Tray | X |  | X |  | 2 x Power Circuit to DGPO
Tackle Store - Dropper Circuits
| Spooling Wall TV x 2 | X |  | X |  | Power Circuit to each TV
| Spooling Wall | X |  | X |  | Fit of lighting in Supplied joinery
| Workshop POS | X |  | X |  | 2 x Power Circuit to DGPO
| Workshop Spooling area | X |  | X |  | 3 x Power Circuit to DGPO
| Sounder Table | X |  | X |  | 1 x Power Circuit to DGPO
7.14 | Supply& Fit Off GPO's
7.15 | Retail & Dock - GPO's | X |  | X |  | General power circuits & double GPOs installed throughout the Retail & Dock Areas as indicated on the Electrical Plan. GPO’s to be installed 300mm above FFL unless indicated on the electrical plan. White GPO's installed to White walls, Black GPO's installed Blue walls
7.16 | Office / Click & Collect Room - GPO's | X |  | X |  | Separate dedicated circuits and double GPO's installed in the Managers Office and Click & Collect Room as indicated on the Electrical Plan.
7.17 |  | X |  | X |  | 1 x Dedicated circuit & 3 x DGPO's with USB & USB -C installed for Manager's Desk
7.18 |  | X |  | X |  | 2 x Dedicated circuit with 2 x DGPO's for the Alarm System
7.19 |  | X |  | X |  | 1 x Dedicated Circuits & 3 x DGPO's for the Data Cabinet
7.2 |  | X |  | X |  | 1 x DGPO - Click & Collect Room
7.21 | Team Room - GPO's | X |  | X |  | 2 x DGPO with USB & USB -C installed to Kitchen splash back
7.22 |  | X |  | X |  | 1 x GPO installed for Microwave
7.23 |  | X |  | X |  | 1 x DGPO with USB & USB-C installed for Training Desk
7.24 |  | X |  | X |  | 1 x DGPO for Vacuum Cleaner
7.25 |  | X |  | X |  | 1 x DGPO undersink for filtered Chilled water system
7.26 |  | X |  | X |  | 1 x Dedicated circuit to Hot Water Unit
7.27 | Auto Door - GPO | X |  | X |  | 1 x GPO |  | N/A - Existing BCF Tenancy Auto door to be used.
7.28 | Air Curtain to Entry | X |  | X |  | 1 x Dedicated Circuit |  | N/A - Existing BCF Tenancy Auto door to be used.
7.29 | Entry EAS Security | X |  | X |  | 1 x GPO 'Install pre-wire for EAS security (including floor chasing at front entrance – if required). |  | N/A - Existing BCF Tenancy Auto door to be used.
7.3 | Roller Door - GPO | X |  | X |  | 1 x GPO |  | N/A - Existing motor and power supply to be utilised.
7.31 | Dock Buzzer & Speakers | X |  | X |  | Dock Buzzer installed with 2 x (moflash) Bell installed in the BOH Doc & on the back wall in retail area of the tenancy. A wired Dock Buzzer is required. - 150mm 96DB Bell or similar
7.32 | Illuminated Signage - Circuits | X |  | X |  | Signage lighting circuits to be wired to enable interfaced with Tenant BMS. Locations as indicated on the Electrical Plan. To be connected to photoelectric cell (PE cell) and analogue 7-day 24-hour time clock Timer to enable signage after 5pm (subject to PE cell activation), Timer to be set to turn off at 10pm each night. Subject to DA restrictions.
7.33 | Pylon Signage | X |  | X |  | Electrical lighting circuits for an externally illuminated Pylon. To be connected to photoelectric cell (PE cell) and analogue 7-day 24-hour time clock Timer to enable signage after 5pm (subject to PE cell activation), Timer to be set to turn off at 10pm each night. Subject to DA restrictions. |  | Existing communal pylon to be utilsied. LL to confirm additional sigange opportunities for BCF at existing signage zones across tenancy. E.g. external building corners.
8 | Communications |  |  |  |  | Refer Communications Schedule
8.01 | NTD / MBF / IDF | X |  | X |  | Requirement installed - NBN NTD (Network Termination Device), MDF (Main Distribution Frame), or IDF (Intermediate Distribution Frame) positioned in the tenancy adjacent the Electrical Switchboard.
8.02 | Cabling conduit | X |  | X |  | Install conduit and pull through cable from the building to the street for connection.
8.03 | Cabling | X |  | X |  | Loop Cable From NBN NTD to Tenant Data Cabinet Location in office Terminate to Port 48 Panduit Patch Panel to be terminated in yellow RJ45 keystone jack
8.04 | Connection Specification | X |  | X |  | Refer to Communications schedule for the preferred connection specification. The exact specification available to the site is to be determined no less than 6 weeks prior to Handover Date and Tenant advised as soon as possible. Should there be an instance where none of the specifications outlined in the Communications schedule are available, the Landlord must advise the Tenant immediately
8.05 | Lead In | X |  | X |  | Contact and advise the appropriate Network provider to attend and connect services (Lead In) by the builder.
8.06 | NBN LOC ID | X |  | X |  | Communications equipment Installed no later than 3 weeks prior to handover to Tenant Provide the NBN LOC ID for the tenancy
9 | Data
9.01 | Retail Area - Dropper Data Cabling (rough in only) |  |  |  |  | CAT 6E Data Cabling for droppers throughout the Retail & Dock Areas as indicated on the Electrical Plan. Data to be run back to Data Rack. Dropper cabling to be left with a 10m tail for later connection at the setup. |  | All Data by Tenant from internal building supply point.
9.02 | Sales Counter |  | X |  | X | 5 x Double Data
9.03 | Click & Collect Counter |  | X |  | X | 1 x Double Data
9.04 | Doc Area |  | X |  | X | 1 x Double Data
9.05 | Fishing Real Counters |  | X |  | X | 2 x Double Data
9.06 | Tackle Store Spooling Wall TV x 2 |  | X |  | X | 1 x Double Data to each TV
9.07 | Tackle Store Workshop POS |  | X |  | X | 1 x Double Data
9.08 | Supply & Fit Off Data |  |  |  |  | Supply & Fit Off - 'Data installation to be CAT 6E cabling with RJ45 Gang Plate Data to be run back to Data Rack
9.09 | Office |  | X |  | X | 2 x Double Data to Managers Desk 850mm from FFL
9.1 |  |  | X |  | X | 1 x Double Data to Alarm system
9.11 |  |  | X |  | X | 1 x Double Data to Cabinet - From NBN NTD
9.12 | Entry |  | X |  | X | 1 x Data Above Auto Doors
9.13 | Security |  | X |  | X | 1 x Double Data to Alarm system
9.14 | Team Room |  | X |  | X | 1 x Data Training Desk
9.15 | Wireless Access Point |  | X |  | X | 1 x Data Grid Ceiling - RJ45 - to be terminated into ceiling Open Ceiling - RJ45 - Access points are to be pole mounted and dropped to height specified
9.16 | Data Rack with Patch Panel |  | X |  | X | To Tenant Spec & Layout (refer plans and supporting documentation) To be located in a conditioned space per Tenant plans. 'Install labelling to Data Rack, Switches, EDB, Electrical & Data Serer Edge 22RU - PART NUMBER: CBN-22RU-66FS
9.17 | EAS Gates |  | X |  | X | 1 x data to EAS gates
10 | Security (rough in)
10.01 | Dropper Data Cabling (rough in only) |  | X |  | X | CAT 6E Data Cabling for droppers throughout the Retail & Dock Areas as indicated on the Electrical Plan. Data to be run back to Data Rack. Dropper cabling to be left with a 6m tail for later connection at the setup. |  | All Security cabling and equipment by Tenant
10.02 | Security Data |  | X |  | X | Open Ceiling Supply and install Cat 6E Data Cabling for security alarm, CCTV equipment 1 x Data to Each Camera coiled and ladled - Minimum 24 Pole Mount - to be coiled & terminated at a height specified on markup typically 3500mm Bulkhead/Horizontal arm mount - to be coiled & terminated within bulkhead ensuring enough length in cable for installation QTY, Location & mount type to be specified - Average 24 Cameras
|  | N/A | N/A | N/A | N/A | Grid Ceiling Supply and install Cat 6E Data Cabling for security alarm, CCTV equipment 1 x Data to Each Camera coiled and ladled - Minimum 24 RJ45 - to be terminated into ceiling QTY, Location & mount type to be specified - Average 24 Cameras |  | N/A - Open ceiling
10.03 |  |  | X |  | X | 1 x Double Data to Each HDMI Extender NVR, Loop cable From Data Cabinet to Asset Protection Screen/Monitor HDMI Extender Qty to be Spec'd by Asset Protection
10.04 |  |  | X |  | X | 2 x Data to Solution 6000, Loop cable from Data Cabinet to solution 6000 Wall unit.
10.05 | Services Interface to Alarm | X |  | X |  | Interface to Lighting circuit / BMS for activation on alarm. Tenancy Distribution board to be provided with 12V relay to enable Lighting to come on when alarm system is activated (Relay P/N OMRMY4NDC12. BASE P/N OMPPYFOSAA-D) 12V FIGURE 8 cable to be run from relay to alarm panel. Connected to alarm panel by Tenant security contractor. Cameras, alarm, keypads etc. will be supplied and installed by Tenant nominated contractor at Tenant cost. |  | Interface cabling and realy by LL for Lighting circuit
11 | Fit out Plumbing / Hydraulic
11.01 | Above Slab Hydraulics | X |  | X |  | To suit Tenant Layout (Refer plans and supporting documentation)
11.02 | Under Slab Hydraulics | X |  | X |  | To suit Tenant Layout (Refer plans and supporting documentation) |  | Existing service points to be utilised.
11.03 | Water supply | X |  | X |  | To architectural fitout design. Water supply tap for plumbed fridge if noted on kitchen layout plan (Refer plans and supporting documentation) Roof tap point for solar panel cleaning (where Solar installation is applicable)
11.04 | Instantaneous Hot Water system | X |  | X |  | Install an energy efficient on demand electric hot water system under the sink to provide hot water, including to the toilet hand basin.Stiebel DHCE Series or equivalent Over flow tray Isolation tap All new sites or refurbishments are to be all-electric with no gas used for DHW. Any existing Gas heating systems are to be replaced with electric.
11.05 | Water Efficiency | X |  | X |  | Provision of high Water Efficiency Rating Scheme (WELS) rated fixtures, fittings and appliances ensuring lower building water demand Toilets - Minimum 4 Star dual flush WELS rating Tapware - Minimum 3 Star WELS Rating
11.06 | Chilled Water Tap | X |  | X |  | Supply & install Chilled Zip water tap into Kitchen - CT1501-1 ChillTap 140 0.2mic Commercial
12 | Lighting supply and install |  |  |  |  | To Tenant Spec & Layout (refer plans and supporting documentation when available) - to be compliant with AS1680
12.01 | Lighting controls | X |  | X |  | To Tenant Spec & Layout, Light switches are required at Tenancy entry point, confirm with Tenant staff entry point location. Interface into BMS where nominated.
12.02 | Lighting Circuits (rough in) | X |  | X |  | Run Circuits to all lighting throughout as indicated on the Lighting Plan. Including all Suspended Feature Lighting
12.03 | Lighting Design | X |  | X |  | Supply a Lighting design to achieve minimum lux levels, based on fixture layout and racking height (post fixture installation), joinery and service locations/heights throughout the tenancy. Landlord responsible to provide final lighting design, heat map and confirmation of compliance to NCC power density requirements for artificial lighting and power for approval by Tenant. Refer Architectural Schedules for fitting types and attached Lighting and controls Specification for Lux levels throughout. |  | All lights fed from tenancy EDB to be LED, any non LED to be replaced.
12.04 | Retail & Dock Lighting - Open Ceiling | X |  | X |  | To Tenant Spec & Layout - to be compliant with AS1680 120 w LED - APRILLA HIGHBAY LED hung on wire from roof purlins; Preferred Lighting Supplier - Specialised Lighting Solutions Installed to account for Tenancy conditions and lighting design. preferred height 5500 to 6000mm above finished floor level (FFL) as indicated on the Lighting Plan. Heights to be approved by Tenant Minimum of 700 lux level, based on fixture layout and racking height (post fixture installation). Preferred Lighting Supplier - Specialised Lighting Solutions - Mark Cassar 0407 632 392 mark.cassar@lh.com.au |  | Remove and Re- use existing LED high bays in BOH area only. New lighting to retail area to tenant specification and layout.
12.05 | Retail Fishing Rod Area Lighting height | X |  | X |  | Minimum 5.5 Metres from FFL to allow for display fishing rods above fixtures - TBC with Tenant prior to installation
12.06 | LED Track Lighting | X |  | X |  | To Tenant Spec & Layout - to be compliant with AS1680 To Suspended Image Panels as per Plan
12.07 | Retail Light Switch | X |  | X |  | Light switch - confirm Entry Door location of Security Key Pad
12.08 | Team Room Lighting | X |  | X |  | Motion Sensor - 30 minute intervals Minimum of 400 lux is required 36 watt Monaco LED Panelite Light Fittings as indicated on the Lighting Plan.
12.09 | Manager's Office Lighting | X |  | X |  | Motion Sensor - 30 minute intervals Minimum of 400 lux is required 36 watt Monaco LED Panelite Light Fittings as indicated on the Lighting Plan.
12.1 | Bathroom Lighting | X |  | X |  | Motion Sensor - 30 minute intervals Minimum of 400 lux is required 36 watt Monaco LED Panelite Light Fittings as indicated on the Lighting Plan.
12.11 | Security Relay Lighting Control | X |  | X |  | A 12V relay to be installed into the switchboard to enable lighting to come on when alarm systems are activated (relay – P/N OMRMY4NDC12. Base P/N OMPPYFOSAA-D). 12V figure 8 cable to be run from relay to manager office, cable tail to be made safe and left in ceiling above office. (connected by others).
12.12 | External lighting | X |  | X |  | External LED lighting under awnings and above external exits sufficient to maintain satisfactory security and safety standards and include the installation of PE cells and an analogue 7 day 24 hour time clocks. Details to be provided to the Tenant for review and approval.
12.13 | Hard bays lighting (Carpark) | X |  | X |  | Final lighting design to be approved by Tenant. |  | LL common area, power by LL.
12.14 | Exit and Emergency Lighting | X |  | X |  | LED Emergency Exit and evacuation lighting in accordance with NCC and AS2293.1. Location of emergency exit and evacuation lighting to take into consideration fixture layout and permitted use. Provide test switch facilities on distribution boards to comply with AS2293. Wired back to the Tenancy EDB Provide a completed log book (General Lighting Service or equal). Exit Lighting: Clevertronics Ultrablade Pro Surface Mount per Tenant Lighting specification. Emergency Lighting: New stores to be provided with the following Non-Maintained Emergency Lighting: Tiled or Plaster Ceilings Clevertronics Lifelight Recessed High / Exposed Ceilings Clevertronics Lifelight Surface Mount Warehouse Lens Light Existing emergency lighting can be retained in store renewals provided: • All existing emergency lighting is LED • All existing emergency lighting is not configured as “Maintained” |  | Existing Exit and emergency lighting may be reused, reconfigured by LL as required for compliance to Tenant layout. Where additional EEL required this is by LL to suit tenant layout.
12.15 | Landlord Requirements | X |  | X |  | Provide a completed log book (General Lighting Service or equal).
12.16 |  | X |  | X |  | Label all light switches, GPO's and Data face plates throughout the tenancy
12.17 |  | X |  | X |  | Signage analogue 7-day 24-hour time clock & PE Cell
12.18 |  | X |  | X |  | For the Retail & Dock areas of the tenancy electrical wiring for lighting circuits shall be configured to enable two operating modes - Trading mode and Non -Trading mode. For Trading mode, the lighting system shall provide a minimum light level of 700 lux. In Non-trading mode, the lighting system shall provide a minimum lux level of 160 lux (or AS1680 standard equivalent) and approximately every one in three fittings is connected to the non-trading circuit. Final lighting design to be approved by Tenant. |  | Tenancies to remain on separate switches, switches for whole premises to be adjacent each other per tenant nominated entry point.
12.19 |  | X |  | X |  | Lighting system shall provide an average light level of 700 lux at FFL after fixtures have been installed
12.2 |  | X |  | X |  | Total store lighting intensity shall comply with National Construction Code Section J
12.21 |  | X |  | X |  | Unless otherwise specified all light fittings to be LED - Refer to the Tenant's Lighting Plan and Specification.
Internal works
13 | Retail Area |  |  |  |  | To Tenant Spec & Layout (refer plans and supporting documentation when available)
13.01 | Partition Walls & Finishes | X |  | X |  | To Tennant 's Layout and engineers specification. Refer Plans. Perimeter Walls to be Gyprock sheeted to underside of Roof or minimum 6000mm & Insulated BoH Partition: Stud wall full height, lined both sides, with insulation minimum total R-1.4. InternalPartition : Stud wall lined both sides, no insulation unless required for acoustics. Developer is responsible for ensuring appropriate Fire Separation and HVAC / Smoke Exhaust operation with respect to any inter or intra-tenancy walls. |  | Demolish existing IT wall back to where new BOH wall joins. Keep rear section of IT wall for use as BOH wall to new layout. Make good floor and ceiling as required following demolition.
13.02 | Door | X |  | X |  | To Tenant's Layout
13.03 | Open Ceiling | X |  | X |  | No Ceiling - Open Plan
13.04 | Flooring & Skirting |  | X |  | X | Polished Concrete - Mechanical Surface Polish Minimal to light Stone Exposure: No or Minimal stone visibility to resemble salt and pepper look, mechanically polished, not burnished. Mechanical Grinding (Level 1 to 2): The surface is ground with bonded abrasives, exposing the stone and refining the finish with each cut of concrete floors surface. Satin/Mid-Gloss Finish Provide P2 Slip Rating & Slip Rating Certificate '100mm Black vinyl featheredge skirting Preferred Contractor - ProGrind - Contact Sal Bellissimo sal@progrind.com.au |  | 2204GD - Floor finish'Tenant Works. Floor finish to be left as is by Tenant on completion of lease.
13.05 | Mezzanine Level - if applicable | X |  | X |  | Landlord to provide full detailed engineered drawings of proposed mezzanine level Floor Structure, Stairs, Handrails, Kick Fall protection Carpet or vinyl tiles as agreed with Tenant- Specification TBC with Tenant |  | N/A - No mezzanine
14 | Offices |  |  |  |  | To Tenant Spec & Layout (refer plans and supporting documentation when available)
14.01 | Partition Walls & Finishes | X |  | X |  | External Walls to Min 3600H - Open ceiling - Height To match If Datum Line is higher than 3600H up to 4200H Note Ceiling hangers/bracing not visible from the retail area of the tenancy |  | Managers office ceiling to be plasterboard to avoid visible hangers from reatil space due to location of office. Where Office wall adjoins shopfront glazing, walls to be fully framed and sheeted in.
14.02 | Door | X |  | X |  | 920mm Clear opening Solid Core door 3 x hinge pins Manual digital lock Code locks CL425 SS PVD keyed Mortice lock with internal lever Auto Closer Peep Hole Door Stop
14.03 | Suspended Ceiling | X |  | X |  | Ceiling 3000mm above finished floor level (FFL). Suspended Grid ceiling including solid plasterboard tiles installed. Note Ceiling hangers not visible from the retail area of the tenancy |  | N/A - plasterboard ceiling to Managers office.
14.04 | Flooring & Skirting | X |  | X |  | Vinyl Plank - Poly Flor Mi Plank 9413 Sassafras 185 x 1505mm 100mm Grey vinyl featheredge skirting
15 | Click & Collect room |  |  |  |  | To Tenant Spec & Layout (refer plans and supporting documentation when available)
15.01 | Partition Walls & Finishes | X |  | X |  | External Walls to Min 3600H - Open ceiling - Height To match If Datum Line is higher than 3600H up to 4200H Note Ceiling hangers/bracing not visible from the retail area of the tenancy |  | Where click and collect wall adjoins shopfront glasing, walls to be fully framed and sheeted in.
15.02 | Door - If Required | X |  | X |  | 920mm Clear opening Manual digital lock Code locks CL410 SS PVD, with internal lever Auto Closer Door Stop |  | Door required
15.03 | Ceiling | X |  | X |  | Open Ceiling
15.04 | Flooring & Skirting |  | X |  | X | Polished Concrete - Mechanical Surface Polish Minimal to light Stone Exposure: No or Minimal stone visibility to resemble salt and pepper look, mechanically polished, not burnished. Mechanical Grinding (Level 1 to 2): The surface is ground with bonded abrasives, exposing the stone and refining the finish with each cut of concrete floors surface. Satin/Mid-Gloss Finish Provide P2 Slip Rating & Slip Rating Certificate '100mm Black vinyl featheredge skirting Preferred Contractor - ProGrind - Contact Sal Bellissimo sal@progrind.com.au |  | 2204GD - Floor finish'Tenant Works. Floor finish to be left as is by Tenant on completion of lease.
16 | Team room |  |  |  |  | To Tenant Spec & Layout (refer plans and supporting documentation when available)
16.01 | Partition Walls & Finishes | X |  | X |  | External Walls to Min 3600H - Open ceiling Walls To match If Datum Line is higher if wall is in the retail space Note Ceiling hangers/bracing not visible from the retail area of the tenancy |  | New Team room in existing location per Tenant layout. Existing to be demolished as too small. Re-use existing bathroom wall as applicable.
16.02 | Door | X |  | X |  | 920mm Clear opening Manual digital lock Code locks CL410 SS, internal lever with latch Auto Closer Peep Hole Door Stop Stainless Kicker to internal
16.03 | Suspended Ceiling | X |  | X |  | Ceiling 3000mm above finished floor level (FFL). Suspended Grid ceiling including solid plasterboard tiles installed. Note Ceiling hangers not visible from the retail area of the tenancy
16.04 | Flooring Finish & Skirting | X |  | X |  | Vinyl Plank - Poly Flor Mi Plank 9413 Sassafras 185 x 1505mm 100mm Grey vinyl featheredge skirting
16.05 | Kitchenette | X |  | X |  | To Tenant's Spec & Layout Kitchen cabinetry and splash back Top Joinery Colours to suit Brand as per detail Single sink with Drainer Flick mixer with isolation taps Zip Tap - Chiller Water |  | Existing kitchenette / team room is not large enough. Existing to be demolished and replaced to new BCF specification. Adjoining existing bathroom partition wall to remain.
17 | Fitting Rooms |  |  |  |  | To Tenant Spec & Layout (refer plans and supporting documentation when available)
17.01 | Design | X |  | X |  | Size & Design of DDA Accessible unisex fitting room to be in accordance with AS1428.1 & NCC Section F Health & Amenity, Spec 27 Accessible adult change facilities. Provide & locate statutory ‘Unisex Change Room’ signage in accordance with BCA & NCC.
17.02 | Partition walls & finishes | X |  | X |  | External Walls to Min 3600H - Open ceiling - Height To match If Datum Line is higher than 3600H up to 4200H Note Ceiling hangers/bracing not visible from the retail area of the tenancy
17.03 | Door | X |  | X |  | DDA Accessible fitting room door openings shall be minimum 850mm clear with door hardware, privacy snibs to be in accordance AS1428.1. Preferred Lever Latch Spec: Carbine PR6030 Lever Privacy Set (or similar). Single action release. Ensure hinged door access panel size is 100mm offset from FFL & 100mm lower offset from wall top plate allow fitting room air flow
17.04 | Suspended Ceiling | X |  | X |  | Ceiling 3000mm above finished floor level (FFL). Suspended Grid ceiling including solid plasterboard tiles installed.
17.05 | Flooring Finish & Skirting |  | X |  | X | Fitting room floor to be finished the same as retail area throughout the tenancy. |  | 2204GD - Floor finish'Tenant Works. Floor finish to be left as is by Tenant on completion of lease.
17.06 | Mirror | X |  | X |  | Full Length Silver Mirror with Safety Viny back/ESG rated. Mirror Size 650mm x 1650H, mounted 300mm from FFL. Must be Framed
17.07 | Clothing Hooks & Accessories | X |  | X |  | Supply & install 2x clothing hooks & 1650H @ 500mm spacing, Specification: Concealed Fix Coat Hook Code: P0805 Supplier: Entro (or similar)
18 | Bathrooms |  |  |  |  | To Tenant Spec & Layout (refer plans and supporting documentation when available)
18.01 | Design | X |  | X |  | Bathrooms to be supplied as per AS1428.1-2009 and current Building Code of Australia |  | Existing Bathroom to be utilised - To be cleaned Repaint walls Keep existing toilet and railings if meets DDA compliance. Replace fittings and fixtures throughout including basin and mirror.
18.02 | Partition walls & finishes | X |  | X |  | External Walls to Min 3600H - Open ceiling Walls To match If Datum Line is higher if wall is in the retail space Note Ceiling hangers/bracing not visible from the retail area of the tenancy |  | Existing Bathroom to be utilisedis - To be cleaned Repaint walls
18.03 | Door | X |  | X |  | Solid Core Toilet lever with latch, Carbine PR6030 Lever Privacy Set Auto Closer Door Stop Stainless Kicker to internal |  | Utilise existing door, add auto Closer, stops and kicker. Repaint door
18.04 | Ceiling | X |  | X |  | Fixed plasterboard ceiling 2700mm - 3000mm above finished floor level (FFL). |  | Keep existing
18.05 | Flooring finish incl Skirting | X |  | X |  | Refer Tenant Architectural plans for nominated floor finishes and skirting throughout. |  | N/A - Existing
18.06 | Fixtures & Fittings | X |  | X |  | AS1428.1 Required signage
|  | X |  | X |  | AS1428.1 Toilet pan
|  | X |  | X |  | AS1428.1 Wash basin - Caroma Cube extension wall basin (864105W) or similar
|  | X |  | X |  | AS1428.1 water efficient tapware
|  | X |  | X |  | AS1428.1 Handrail
|  | X |  | X |  | AS1428.1 Toilet roll holder
|  | X |  | X |  | Mirror above Wash basin
|  | X |  | X |  | Soap & Paper Towel Dispenser
18.07 | If Existing Bathrooms | X |  | X |  | Existing to remain, any modifications required by Landlord at Landlord Cost
|  | X |  | X |  | Bathrooms to be supplied as per AS1428.1-2009 and current Building Code of Australia
19 | Stock/Store Room |  |  |  |  | To Tenant Spec & Layout (refer plans and supporting documentation when available)
19.01 | Partition Wall & Finishes | X |  | X |  | To Tenant 's Layout storeroom dividing wall to retail area Partition wall to be created to underside of purlin with painted gyprock to Tenant specification on the retail side and clear coated 12mm structural ply B/C appearance grade on storeroom side with insulation, minimum total R-1.4. (B-Grade finish exposed side)
19.02 | Door | X |  | X |  | To Tenant's Layout
19.03 | Open Ceiling | X |  | X |  | No Ceiling - Open Plan
19.04 | Stock room doors | X |  | X |  | Flex shield 350 series PVC Door 2700H x 1800W. 7mm NT PVC Grey to 1400H and then clear to 2700H include Magnet catches
19.05 | Flooring & Skirting |  | X |  | X | Polished Concrete - Mechanical Surface Polish Minimal to light Stone Exposure: No or Minimal stone visibility to resemble salt and pepper look, mechanically polished, not burnished. Mechanical Grinding (Level 1 to 2): The surface is ground with bonded abrasives, exposing the stone and refining the finish with each cut of concrete floors surface. Satin/Mid-Gloss Finish Provide P2 Slip Rating & Slip Rating Certificate '100mm Black vinyl featheredge skirting Preferred Contractor - ProGrind - Contact Sal Bellissimo sal@progrind.com.au |  | 2204GD - Floor finish'Tenant Works. Floor finish to be left as is by Tenant on completion of lease.
20 | Floor Finish - Polished Concrete
20.01 | Preparation | X |  | X |  | Floor must be dry and swept clean of all dust and all other loose materials such as concrete, paint, plaster and mortar droppings.
20.02 | Preparation | X |  | X |  | Concrete must be free of all grease, bond breaking agents, oil and other contaminants (note: if concrete is not free of contaminates, grinding to remove such materials will be required so as to prevent interference with bonding with the concrete - costs of such subsequent grinding and priming will be borne by the Landlord).
20.03 | Expansion Joints & Saw Cuts |  | X |  | X | POLYUREA sealant/filter to expansion joints and saw relief cuts to match existing concrete colour. |  | 2204GD - Floor finish'Tenant Works. Floor finish to be left as is by Tenant on completion of lease.
20.04 | Polished Concrete Flooring - Retail, Dock, and Click & Collect Areas |  | X |  | X | Polished Concrete - Mechanical Surface Polish Minimal to light Stone Exposure: No or Minimal stone visibility to resemble salt and pepper look, mechanically polished, not burnished. Mechanical Grinding (Level 1 to 2): The surface is ground with bonded abrasives, exposing the stone and refining the finish with each cut of concrete floors surface. Satin/Mid-Gloss Finish Provide P2 Slip Rating & Slip Rating Certificate '100mm Black vinyl featheredge skirting Preferred Contractor - ProGrind - Contact Sal Bellissimo sal@progrind.com.au |  | 2204GD - Floor finish'Tenant Works. Floor finish to be left as is by Tenant on completion of lease.
20.05 | Slip Rating |  | X |  | X | Appropriate slip rating must be achieved to meet AS, minimum P2 slip rating, wet pendulum test for internal. Slip test results to be provided prior to Handover |  | 2204GD - Floor finish'Tenant Works. Floor finish to be left as is by Tenant on completion of lease.
20.06 | Skirting |  | X |  | X | 100mm Black vinyl featheredge skirting to the base of the walls throughout the tenancy. |  | 2204GD - Floor finish'Tenant Works. Floor finish to be left as is by Tenant on completion of lease.
20.07 | Click & Collect Room |  | X |  | X | Click & Collect room floor to be finished the same as retail area throughout the tenancy. |  | 2204GD - Floor finish'Tenant Works. Floor finish to be left as is by Tenant on completion of lease.
21 | Painting
21.01 | Painting Requirements | X |  | X |  | All painting to be completed to a commercial standard in accordance with the manufacturer’s instructions. Surfaces to be suitablely prepared and primed / sealed prior to application. Dulux Contact -Lauren de Graaf 0447 551 962 email: lauren.deGraaf@dulux.com.au All exposed services, grilles, ductwork etc. colours as nominated in Tenant Plans.
21.02 | External painting |  | X |  | X | Building to Tenant specification minimum 1 x Sealer coat & 2 coats (Tenant to provide Mock-up) External surfaces to be pressure cleaned prior to painting Dulux Weather shield Low Sheen, Satin Acrylic Dulux BCF Next Gen Blue” and Dulux BCF Orange Dulux Contact -Lauren de Graaf 0447 551 962 email: lauren.deGraaf@dulux.com.au |  | 2204GD - LL to provide surfaces to Tenant cleaned and ready to paint. Painting by Tenant.
21.03 | Carpark Bump Stops | X |  | X |  | Dulux Safety Yellow (Pantone PMS 7405) |  | LL to undertake all external painting to both tenancies.
21.04 | Carpark Gutters & Steps | X |  | X |  | Dulux Safety Yellow (Pantone PMS 7405) |  | LL to undertake all external painting to both tenancies.
21.05 | Internal painting | X |  | X |  | To Tenant Spec & Layout (refer plans and supporting documentation) Minimum 1 x undercoat & 2 x coats of topcoat All exit doors to be painted to match external livery to comply with building regulations. (30% variation to surrounding wall colour)
21.06 | Retail Area Walls & Columns | X |  | X |  | FFL to Datum Line – Dulux BCF Next Gen Blue - Dulux Wash & Wear Low Sheen - Satin Acrylic Datum Line to Roof/Ceiling Taubman's cotton touch low sheen • Datum line 3800mm for sites with lowest roof point between 4000mm to 5000mm • Datum line 4200mm for sites with lowest roof point 5000mm and above • Datum line TBC - Roof below 4000mm or ceiling installed All exit doors to be painted to match external livery to comply with building regulations. (30% variation to surrounding wall colour).
21.07 | Click & Collect Room | X |  | X |  | Walls Taubman's cotton touch low sheen Doors Dulux BCF next gen blue gloss Door frames and architrave, located within the tenancy Taubman's cotton touch Gloss
21.08 | Team Room | X |  | X |  | Walls Taubman's cotton touch low sheen One Wall - Dulux BCF Next Gen Blue Doors Dulux BCF next gen blue gloss Door frames and architrave, located within the tenancy Taubman's cotton touch Gloss
21.09 | Office | X |  | X |  | Walls Taubman's cotton touch low sheen Ceiling Taubman's cotton touch low sheen Doors Dulux BCF next gen blue gloss Door frames and architrave, located within the tenancy Taubman's cotton touch Gloss
21.1 | Bathroom | X |  | X |  | Walls Taubman's cotton touch low sheen Ceiling Taubman's cotton touch low sheen Doors Dulux BCF next gen blue gloss Door frames and architrave, located within the tenancy Taubman's cotton touch Gloss
21.11 | Store Room / Dock Area | X |  | X |  | Stock storeroom partition wall to be created to underside of purlin with painted gyprock to Tenant specification on the retail side and clear coated 12mm structural ply on storeroom side.
21.12 | Columns & Handrails - Free standing | X |  | X |  | Dulux BCF Blue Low Sheen
21.13 | Columns on Perimeter Walls | X |  | X |  | Columns to Perimeter walls to match wall colour
21.14 | Internal exposed main beams and secondary beams/purlins | X |  | X |  | To match insulation (white/silver/ grey), seek approval from Tenant on finish. |  | Not required - Keep existing Silver and Blue. Touch up any damged areas to match.
21.15 | Perimeter Walls - Internal & External | X |  | X |  | Services such as conduits, down pipes & any item along walls, painted to match wall colours
22 | Renewable Energy Power Supply
22.01 | Direct behind the meter rooftop solar PV system. | X |  | X |  | Minimum 30kW Behind the meter rooftop solar system to tenancy. Inverter and Panels to comply with SRG responsible sourcing requirements to be approved by Tenant prior to procurement. Refer Tenant Solar specification. |  | 2204GD - No solar at this site
23 | Completion of Landlord Works
23.01 | Landlord to carry out the above works at the Landlords cost prior to the Tenant taking handover
23.02 | Tenancy to be professionally cleaned prior to handover including Team Room, Offices, Amenities, Shopfront, Glazing, Carpark, Footpaths, External Shopfront, Etc.
23.03 | The premises to be clear and cleaned of all the outgoing tenants’ equipment, fittings, fixtures, wall, ceiling and floor surfaces
Comments
The purpose of the Annexure C - Landlord Scope is to define the ownership, division of work, cost allocation, maintenance, etc. for the premises.
In case of any discrepancy between the "body of Lease Agreement" and the "Annexure C - Landlord's Scope" in relation to the scope of works the "Demarcation list" shall prevail.
All works will be done according to Tenant's standards or/and as directed by Tenant's Project Manager in accordance with local legislation
The description of the works, quality and material are as defined in accordance with the Tenant brand Architectural drawing package and any specifications and standard guidelines provided by Tenant
Climate Zones as per NCC Climate Zone map, Refer ABCB for latest update interactive map: https://www.abcb.gov.au/abcb-climate-map
Remarks*
Where there is any Landlord contribution payable, Tenant will pay the Tenant's Contractor directly in accordance with the Contract Agreement Setout in Milestone payments. The Landlord will pay Tenant Directly in Milestones throughout the Project the agreed capped Contribution amount towards the Fit out. The Landlord will not withhold payment to the Tenant and will settle invoice payments within 14 days or receipt of Invoice from the Tenant.
Definitions
(SRG): Super Retail Group
(LL): Landlord
(T): Tenant

## DELIVERY REQUIREMENTS v1.0
Most Common Trucks to deliver to BCF |  | Version 1.0 Dated 22/10/2025
12PLT PTG | (Power Tail Gate)
Overall length of vehicle including cabin – 10m
Total height of body – 4.3m
Total width – 2.3m
Dimensions of (full size) PTG – 2.3m x 2.9m
Overall length of vehicle including cabin & PTG lowered – 12.9m
14PLT PTG
Overall length of vehicle including cabin – 11.2m
Total height of body – 4.3m
Total width – 2.3m
Dimensions of (full size) PTG – 2.3m x 2.9m
Overall length of vehicle including cabin & PTG lowered – 14.1m
NOTE: PTG must be taken into consideration for dock length to ensure truck is not impeding road ways or access
NOTE: Any weight restrictions and height restrictions for trucks must be taken into consideration by Landlord. (BCF need to be able to safely get trucks to dock location)

## GAS DECANTING AREA
SUBJECT TO APPROVAL BY SRG AND ORIGIN ENERGY